| Document Reviewed: NYSTA Exit 37 Plans and Structural Analysis Report Exit 37. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location: I-90 Exit 37 |  |  |  |  |  |  |  |
| Address: I-90 Exit 37 Liverpool, NY 13088 |  |  |  |  |  |  |  |
| INITIATOR: | NYSTA | Date: | 8/27/2025 | RESPONDER: |  | Date: |  |

| Action Code Key |  | A | B |  | C |  | N/A |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Designer will Comply | Designer will Evaluate |  | Comment Not Incorporated |  | Comment Not Applicable |
| No. | Drawing No. or Spec. Section | Comments |  | Action |  | Responses |  |
|  |  | NYSTA EXIT 37 PLANS |  |  |  |  |  |
| 1. | T01 | Acceptable building codes and standards- 2018 international building code and 2018 International Mechanical code are not acceptable codes and is the old version of the code. Please remove any references to this outdated code. |  |  |  |  |  |
| 2. | T01 | Acceptable building codes and standards- 2020 New York electrical code of New York state is not a listed code of the 2020 New York State building standards and codes and shall be removed. |  |  |  |  |  |
| 3. | T01 | Acceptable building codes and standards- “ANSI/TIA-222-H STRUCTURAL STANDARD FOR ANTENNA SUPPORTING STRUCTURES, ANTENNAS AND SMALL WIND TURBINE SUPPORT STRUCTURES” is not found in chapter 35 of the 2020 building code of new yok state. The closest referenced standard is “222-G—2005: Structural Standards for Antenna Supporting Structures and Antennas”. Review revise as necessary. |  |  |  |  |  |
| 4. | T01 | Acceptable building codes and standards- ANSI/TIA-607-B - GENERIC TELECOMMUNICATIONS BONDING AND GROUNDING (EARTHING) FOR CUSTOMER PREMISES” is not found in chapter 35 of the 2020 building code of New York State. Review revise as necessary. |  |  |  |  |  |
| 5. | T01 | Acceptable building codes and standards- “BUILDING CODE REQUIREMENTS FOR STRUCTURAL CONCRETE” is a separate code reference from ACI 318-14. It shall be listed as its own reference standard ACI 318-14: Building Code Requirements for Structural Concrete as shown in chapter 35 of the 2020 building code of New York State. |  |  |  |  |  |
| 6. | T01 | Acceptable building codes and standards- “IEEE C2: NATIONAL ELECTRICAL SAFETY CODE” is not a listed code in chapter 35 of the 2020 New York State building standards and codes and shall be removed. |  |  |  |  |  |
| 7. | GN01 | General Construction Note- 30- Please revise this note to include Code Compliance for As-Builts to be submitted to as this will be a requirement for the final certificate for this project. |  |  |  |  |  |
| 8. | GN02 | Concrete Masonry Notes- A note shall be added that all Mortar/Grout, shall be tested for strength to ensure the required PSI requirements are met. All reports shall be submitted to Code Compliance. |  |  |  |  |  |
| 9. | GN02 | Concrete Masonry Note- 33- Section 2104.6.1 of the 2020 Building Code of New York State does not exist. This chapter only goes up to 2104.1.2. Review/revise as necessary. |  |  |  |  |  |
| 10. | GN02 | Structural concrete notes- A note shall be added that all concrete, no matter how many yards are poured, shall be tested for strength to ensure the required PSI requirements are met. All reports shall be submitted to Code Compliance. |  |  |  |  |  |
| 11. | GN02 | Structural Steel notes- A note shall be added that all reenforcing steel shall be inspected by a third party and reports submitted to Code Compliance. |  |  |  |  |  |
| 12. | A04 | Mount Analysis Notes not provided for review. |  |  |  |  |  |
| 13. | A14 | Canopy/platform plans shall include all seismic design loads for this area, construction and foundation plans. |  |  |  |  |  |
| 14. | G02 | Grounding Notes- 4- Code compliance shall be added to the distribution list. |  |  |  |  |  |
|  |  | Structural Analysis Report |  |  |  |  |  |
| 15. | Sheet 1 | Reference to the 2020 New York State Uniform Code shall be changed to the 2020 Building Code of New York State. |  |  |  |  |  |
| 16. | Sheet 1 | The engineer’s registration expiration date is a requirement that shall be added to the stamp and signature. |  |  |  |  |  |
| 17. | Sheet 5 | Current load criteria shall include snow load. |  |  |  |  |  |
| 18. | General | This report mentions a drilled pier foundation that does not match up with the approved construction plans for the tower. Review/revise as necessary. |  |  |  |  |  |
|  |  | General |  |  |  |  |  |
| 19. | General | Third party electrical inspections are required. Both rough in and final shall be completed and final reports submitted to code compliance. |  |  |  |  |  |
| 20. | General | Construction Permit Application not submitted. |  |  |  |  |  |
| 21. | General | Geotechnical Report not submitted |  |  |  |  |  |
| 22. | General | ASCE Hazard Reports not submitted |  |  |  |  |  |
| 23. | General | Full environmental assessment form not submitted |  |  |  |  |  |