| Document Reviewed: NYSTA Exit 37 Plans and Structural Analysis Report Exit 37. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location: I-90 Exit 37 |  |  |  |  |  |  |  |
| Address: I-90 Exit 37 Liverpool, NY 13088 |  |  |  |  |  |  |  |
| INITIATOR: | NYSTA | Date: | 8/27/2025 | RESPONDER: |  | Date: |  |

| Action Code Key |  | A | B |  | C |  | N/A |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Designer will Comply | Designer will Evaluate |  | Comment Not Incorporated |  | Comment Not Applicable |
| No. | Drawing No. or Spec. Section | Comments |  | Action |  | Responses |  |
|  |  | NYSTA EXIT 37 PLANS |  |  |  |  |  |
| 1. | T01 | Acceptable building codes and standards- 2018 international building code and 2018 International Mechanical code are not acceptable codes and is the old version of the code. Please remove any references to this outdated code. |  |  |  | DRAWINGS UPDATED Closed |  |
| 2. | T01 | Acceptable building codes and standards- 2020 New York electrical code of New York state is not a listed code of the 2020 New York State building standards and codes and shall be removed. |  |  |  | DRAWINGS UPDATED Closed |  |
| 3. | T01 | Acceptable building codes and standards- “ANSI/TIA-222-H STRUCTURAL STANDARD FOR ANTENNA SUPPORTING STRUCTURES, ANTENNAS AND SMALL WIND TURBINE SUPPORT STRUCTURES” is not found in chapter 35 of the 2020 building code of new yok state. The closest referenced standard is “222-G—2005: Structural Standards for Antenna Supporting Structures and Antennas”. Review revise as necessary. |  |  |  | DRAWINGS UPDATED The following is the only listed TIA reference standard that is accepted in chapter 35 of the 2020 New York State Building Code. Review/Revise as necessary. |  |
| 4. | T01 | Acceptable building codes and standards- ANSI/TIA-607-B - GENERIC TELECOMMUNICATIONS BONDING AND GROUNDING (EARTHING) FOR CUSTOMER PREMISES” is not found in chapter 35 of the 2020 building code of New York State. Review revise as necessary. |  |  |  | DRAWINGS UPDATED ANSI/TIA-607-E - GENERIC TELECOMMUNICATIONS BONDING AND GROUNDING (EARTHING) FOR CUSTOMER PREMISES” is not found in chapter 35 of the 2020 building code of New York State. Review revise as necessary. |  |
| 5. | T01 | Acceptable building codes and standards- “BUILDING CODE REQUIREMENTS FOR STRUCTURAL CONCRETE” is a separate code reference from ACI 318-14. It shall be listed as its own reference standard ACI 318-14: Building Code Requirements for Structural Concrete as shown in chapter 35 of the 2020 building code of New York State. |  |  |  | SEE UPDATED DRAWINGS PROVIDED 10.29.25 ACI 318-14, AMERICAN CONCRETE INSTITUTE -318 -14 was removed. Is this no longer being used? Please add this back in if it will be used in the design of these plans. |  |
| 6. | T01 | Acceptable building codes and standards- “IEEE C2: NATIONAL ELECTRICAL SAFETY CODE” is not a listed code in chapter 35 of the 2020 New York State building standards and codes and shall be removed. |  |  |  | SEE UPDATED DRAWINGS PROVIDED 10.29.25 Closed |  |
| 7. | GN01 | General Construction Note- 30- Please revise this note to include Code Compliance for As-Builts to be submitted to as this will be a requirement for the final certificate for this project. |  |  |  | SEE UPDATED DRAWINGS 10.29.25 Closed |  |
| 8. | GN02 | Concrete Masonry Notes- A note shall be added that all Mortar/Grout, shall be tested for strength to ensure the required PSI requirements are met. All reports shall be submitted to Code Compliance. |  |  |  | SEE UPDATED DRAWINGS 10.29.25 Closed |  |
| 9. | GN02 | Concrete Masonry Note- 33- Section 2104.6.1 of the 2020 Building Code of New York State does not exist. This chapter only goes up to 2104.1.2. Review/revise as necessary. |  |  |  | SEE UPDATED DRAWINGS 10.29.25 Closed |  |
| 10. | GN02 | Structural concrete notes- A note shall be added that all concrete, no matter how many yards are poured, shall be tested for strength to ensure the required PSI requirements are met. All reports shall be submitted to Code Compliance. |  |  |  | SEE UPDATED DRAWINGS 10.29.25 Closed |  |
| 11. | GN02 | Structural Steel notes- A note shall be added that all reenforcing steel shall be inspected by a third party and reports submitted to Code Compliance. |  |  |  | SEE UPDATED DRAWINGS 10.29.25 Closed |  |
| 12. | A04 | Mount Analysis Notes not provided for review. |  |  |  | Mount Analysis Notes not provided for review. |  |
| 13. | A14 | Canopy/platform plans shall include all seismic design loads for this area, construction and foundation plans. |  |  |  | SEE UPDATED DRAWINGS 10.29.25 Closed |  |
| 14. | G02 | Grounding Notes- 4- Code compliance shall be added to the distribution list. |  |  |  | APPROVED Closed |  |
|  |  | Structural Analysis Report |  |  |  |  |  |
| 15. | Sheet 1 | Reference to the 2020 New York State Uniform Code shall be changed to the 2020 Building Code of New York State. |  |  |  | SEE SA SENT 10.29.25 Closed |  |
| 16. | Sheet 1 | The engineer’s registration expiration date is a requirement that shall be added to the stamp and signature. |  |  |  | SEE SA SENT 10.29.25 Closed |  |
| 17. | Sheet 5 | Current load criteria shall include snow load. |  |  |  | Engineer of Record response – SA reattached in zip file Closed |  |
| 18. | General | This report mentions a drilled pier foundation that does not match up with the approved construction plans for the tower. Review/revise as necessary. |  |  |  | SEE SA SENT 10.29.25 Closed |  |
|  |  | General |  |  |  |  |  |
| 19. | General | Third party electrical inspections are required. Both rough in and final shall be completed and final reports submitted to code compliance. |  |  |  | PTI & ATT WILL PROVIDE 3rd PARTY REPORTS Closed |  |
| 20. | General | Construction Permit Application not submitted. |  |  |  | SEE ATTACHED Application Project Description shall match the project scope on plans including ground scope of work and antenna level scope of work. Currently items missing that are listed in plans set ground scope of work. |  |
| 21. | General | Geotechnical Report not submitted |  |  |  | SEE ATTACHED Closed |  |
| 22. | General | ASCE Hazard Reports not submitted |  |  |  | SEE ATTACHED Closed |  |
| 23. | General | Full environmental assessment form not submitted |  |  |  | SEE ATTACHED Closed |  |