Document Reviewed: US-NY-2029 NYSTA Exit 37, Structural Design Report, and Geotechnical Investigation Report. Location: Exit 37

Address: I-90 Exit 37, Liverpool, NY 13088

INITIATOR:	Joshua Stagnitti	Date:	6/2/2025 & 6/26/2025	RESPONDER:	Date:

| Action Code Key |  | A | B |  | C |  | N/A |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Designer will Comply | Designer will Evaluate |  | Comment Not Incorporated |  | Comment Not Applicable |
| No. | Drawing No. or Spec. Section | Comments |  | Action |  | Responses |  |

|  |  | CD's have been updated and changes called out CD's have been updated and changes called out A A US-NY-2029 NYSTA Exit 37 |  |  |
| --- | --- | --- | --- | --- |
| 1. | T-1 | Applicable Codes #1- The “International Building Code 2018” was replaced with the 2020 Building Code of New York State. Remove referenced International Building Code 2018 from this list. |  | Closed |
| 2. | T-1 | Applicable Code #3- “Accessibility Code ADA 2015” and “ICC/ANSI A117.1” are not listed in the Reference Standards of Chapter 35 of the 2020 Building Code of New York State. This shall be replaced with the referenced “ICC A117.1-09”. Review/revise as necessary. |  | Closed |
| 3. | T-1 | Applicable Code #5- “Fore/Life Safety Code – IFC 2018” was replaced with the 2020 Fire Code of New York State. Replace with the current version of the code 2020 Fire Code of New York State review/revise as necessary. | A | CD's have been updated and changes called out ATT drawings provided Closed |
| 4. | C-2 | Provide details for what’s in the area marked Future AT&T equipment Area”. This area has 2 different shades and is unclear what is being proposed. No plans have been submitted for any buildings or ice canopies. | N/A | Please confirm that the 20-kw diesel generator, steel platform with canopy is not part of this proposal but will be submitted later for review and permits. |
| 5. | General | Will there be a generator located at this site? Plans and cut sheets will need to be included as part of this review. |  | REFERENCE CARRIER PLANS I could not locate the Carrier plans in the submitted paperwork. Is this a separate plan set or plans within another set of plans? If so please provide location. |
|  |  | A CAISSON IS PREFERRED Structural Design Report |  |  |
| 6. | Page 3 & 4 | Confirm what type of foundation will be used at this site. |  | TBD prior to construction Please notify Code Compliance of what type of foundation will be used once it has been determined. This will be noted as a condition on the construction permit. |

| Action Code Key |  | A | B |  |  | C | N/A |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Designer will Comply | Designer will Evaluate |  |  | Comment Not Incorporated | called out Comment Not Applicable |
| No. | Drawing No. or Spec. Section | Comments |  | CARRIERS WILL PROVIDE INDIVIDUAL SITE PLANS - TMO IS STILL WORKING ON THEIRS will be sent after tower is constructed ATT & VZ ATTACHED Report has been updated and changes N/A A C Action |  | Responses |  |
| 7. | Page 35 | There is reference to Internation Building Code at the top left corner of this page. The internation Code was replaced with the 2020 Building Code of New York State. Review revise as necessary. |  |  |  | Unable to locate the called out item Correction- This item is found in the top left corner of page 35. |  |
| 8. | General | Will there be concrete pads poured for any equipment? No plans have been provided for concrete pads. Provide plans. |  |  |  | Please confirm that no concrete pads will be part of this proposed construction. |  |
|  |  | Geotechnical Investigation Report |  |  |  |  |  |
| 9. | Page 1 of 13 | Amendment to New York State Department of State 19 NYCRR 1203.3(a)(3)(ix) and State Education law for Architects (Article 147) and Engineers (Article 145) the design professionals registration expiration date must be included with submitted construction documents effective December 30, 2020. |  |  |  | Closed |  |
| 10. | Page 2 of 13 | References- “overall site plan, provided by tectonic engineering, dated October 1, 2024”. Submit this site plan for review and cross reference. |  | A |  | Noted site sketch attached with reply submittal Closed |  |
| 11. | General | Confirm what type of foundation will be used at this location. |  | A |  | TBD - CAISSON IS PREFERRED Please notify Code Compliance of what type of foundation will be used once it has been determined. This will be noted as a condition on the construction permit. |  |
|  |  | N/A General Overall Comments |  |  |  |  |  |
| 12. |  | Structural Analysis Reports have not been submitted for review. Please provide reports. |  |  |  | NEW TOWER BUILD-ENGINEERED TOWER DESIGN SUBMITTED WITH CARRIER SPECIFIC LOADING CALLED OUT-TOWER DESIGN TO LOADING Closed |  |
| 13. |  | Hazard Reports have not been submitted. Please provide reports. |  | A N/A |  | Please clarify the request An example of this report from another project has been sent to Jackie Donahue for reference. |  |
| 14. |  | Engineered lift plans have not been submitted. Please provide detailed plans. |  |  |  | LIFT PLAN WILL BE SUBMITTED UPON SELECTION OF A GC & CRANE CO Lift plans are required to be submitted and reviewed by NYSTA Traffic Control for review and approval. |  |
|  |  | ASCE Hazard Reports |  |  |  |  |  |
| 15. | Page 5 of 8 |  |  |  |  | Ground Snow Loads for IRC only, Pg(asd): 58.1 lb/ft2. Ground snow loads for this area are 60 lb./sf. 2020 Building Code of New York State Figure 1608.2. Review revise as necessary. |  |

| Action Code Key |  | A | B |  |  | C | N/A |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Designer will Comply | Designer will Evaluate |  |  | Comment Not Incorporated | Comment Not Applicable |
| No. | Drawing No. or Spec. Section | Comments |  | Action |  | Responses |  |