| Document Reviewed: Verizon- ASCE Hazard Report, Geotechnical Investigation Report, Exit 37 Verizon Drawings, Structural Analysis Report, Construction Permit Application |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location: Verizon Exit 37 |  |  |  |  |  |  |  |
| Address: 460 Electronics Parkway, Liverpool, NY |  |  |  |  |  |  |  |
| INITIATOR: | NYSTA | Date: | 10/03/2025 & 10/10/2025 | RESPONDER: |  | Date: |  |

| Action Code Key |  | A | B |  | C |  | N/A |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Designer will Comply | Designer will Evaluate |  | Comment Not Incorporated |  | Comment Not Applicable |
| No. | Drawing No. or Spec. Section | Comments |  | Action |  | Responses |  |
|  |  | ACSE Hazard Report |  |  |  |  |  |
| 1. |  | No comments at this time. |  |  |  |  |  |
|  |  | Geotechnical Investigation Report |  |  |  |  |  |
| 2. |  | No Comments at this time |  |  |  |  |  |
|  |  | Exit 37 Verizon Drawings |  |  |  |  |  |
|  | T-1 | Project description- This project description shall be consistent and does not match the description on the CP Application. Review Revise. |  | A |  | Revision made. Updated project description box on T-1 to match application. Detailed description has been removed. A fully detailed description shall be given. Description shall note all work and equipment to be added. Application shall match this description. |  |
|  | T-1 | “THIS SET OF PLANS SHALL NOT BE UTILIZED AS CONSTRUCTION DOCUMENTS UNTIL ALL ITEMS OF CONCERN HAVE BEEN ADDRESSED AND EACH OF THE DRAWINGS HAS BEEN REVISED AND ISSUED "FOR CONSTRUCTION".” These Plans cannot be approved as they are not for construction. This section shall be removed, or plans shall be labeled as described “For Construction”. |  | A |  | Drawings are issued “for construction” validating the referenced note. Closed |  |
|  | GN-1 | Concrete Notes- Note 2- Compressive strength of concrete reports shall be submitted to NYSTA Code. Reports are required for all concrete pours regardless of amount of concrete poured. They are required for confirmation that concrete meets the required 4500psi requirement and for final code compliance certificate. |  | A |  | Revision made. Added to new note box on GN-2 labeled “NYSTA SUBMITTAL REQUIREMENTS” Closed |  |
|  | GN-1 | Concrete Notes- Note 4- Third party steel reinforcement inspection is required and reports shall be submitted to NYSTA Code. These reports are required for final code compliance certificate. |  | A |  | Revision made. Added to new note box on GN-2 labeled “NYSTA SUBMITTAL REQUIREMENTS” Closed |  |
|  | GN-1 | Concrete Notes- Note 5- All welding requires to be inspected by a third party. reports shall be submitted to NYSTA Code. These reports are required for final code compliance certificate. |  | A |  | Revision made. Added to new note box on GN-2 labeled “NYSTA SUBMITTAL REQUIREMENTS” Closed |  |
|  | GN-1 | Concrete Notes- Note 11- Concrete slump reports shall be submitted to NYSTA Code. These reports are required for final code compliance certificate. |  | A |  | Revision made. Added to new note box on GN-2 labeled “NYSTA SUBMITTAL REQUIREMENTS” Closed |  |
|  | GN-2 | Grounding Notes- Ground testing reports shall be submitted to NYSTA Code. These reports are required for final code compliance certificate. |  | A |  | Revision made. Added to new note box on GN-2 labeled “NYSTA SUBMITTAL REQUIREMENTS” Closed |  |
|  | GN-2 | Steel Notes- Note 10- All welding requires to be inspected by a third party. reports shall be submitted to NYSTA Code. These reports are required for final code compliance certificate. |  | A |  | Revision made. Added to new note box on GN-2 labeled “NYSTA SUBMITTAL REQUIREMENTS” Closed |  |
|  | C-3 | NOTE: ANTENNA AND HYBRID CABLE SCHEDULE BASED ON AN RF ANTENNA DESIGN SHEET DATED 1/2/25, RFDS PROJECT ID 17326150. Antenna design Seets shall be provided for review. |  | A |  | Zip file package with the antenna, rrh, hybrid, and ovp cut sheets is included in this response. Closed |  |
|  | C-8 | Detail 2- Minimum footer depth shall be 4’ deep to bottom of footer to finish grade. The proposed 3’-6” does not meet this code requirement. Review Revise as necessary. |  | A |  | Revision made. Updated detail 2 on Sheet C-8. Closed |  |
|  | C-9 | Load Criteria such as but not limited to seismic wind speed, snow load etc. Shall be provided for this structure. |  | A |  | Revision made. Added to new note box on C-9 with applicable information. Closed |  |
|  | General | Amendment to New York State Department of State 19 NYCRR 1203.3(a)(3)(ix) and State Education law for Architects (Article 147) and Engineers (Article 145) the design professionals seal, signature, registration expiration date, and when documents are submitted by a professional engineering firm and not a sole practitioner professional engineer, the firm’s Certificate of Authorization number must be included with submitted construction documents effective December 30, 2020. |  | A |  | Revision made. Added registration expiration date under PE stamp in border. Certificate of Authorization number currently in set; located in border, bottom right of Tectonics logo/info. Closed |  |
|  | General | Generator cut sheets shall be provided. |  | A |  | Zip file package with generator cut sheets is included in this response. Closed |  |
|  |  | Structural Analysis Report |  |  |  |  |  |
|  | Page 5 | 6.1 Current Load Criteria- Report does not include snow load. This information does not match up with the ASCE Hazard Report. This information shall be consistent. Review revise as necessary. Inconsistent load criteria also found on Tower Design Notes page 12, 14, 15, & 27. |  |  |  | Engineer of Record response – SA reattached in zip file Closed |  |
|  | General | Amendment to New York State Department of State 19 NYCRR 1203.3(a)(3)(ix) and State Education law for Architects (Article 147) and Engineers (Article 145) the design professionals seal, signature, registration expiration date, and when documents are submitted by a professional engineering firm and not a sole practitioner professional engineer, the firm’s Certificate of Authorization number must be included with submitted construction documents effective December 30, 2020. |  |  |  | SA reattached showing stamp and dates. Closed |  |
|  |  | Construction Permit Application Date 8/27/2025 |  |  |  |  |  |
|  | Project Description | This Project description is inconsistent with the product description on sheet T-1 of the Exit 37 Verizon Drawings. Review revise as necessary. |  |  |  | VZ updated drawings See note 3 above |  |
|  | List of Subcontractors | A list of all subcontractors is required. If there are no other contractors, please add note “No Subcontractors” |  |  |  | Updated permit application in zip file Please provide Verizon Wireless address and contact information. |  |
|  | General | The information on this form will be used for the construction permit. With that said the permit will be issued to Bell Atlantic Mobile System LLC with Jack Redmond as the signee. In the past all permits have been issued to Phoenix Towers International with Jackie Donahue as the signee. If the permit is to be issued to Phoenix Towers International, please make this change and include Bell Atlantic Mobil Systems as the subcontractor. |  |  |  | Updated permit application in zip file Closed |  |